## Slide 1: ELECTRICAL HYGIENIC ENVIRONMENTS

## Slide 2
1
Introduction
2
Hygienic environment classifications
5
Lighting selection & standard
Page 3
Page 4
CONTENTS
Page 8
Equipment enclosures
Cable tray installation good method
4
3
X
Page 7
Page 5
About PMG Engineering
#

## Slide 3: Introduction
Electrical hygienic
Machinery is installed to prepare food and feeding stuffs, electrical power and automation is usually used. This infrastructure must be so designed and constructed that it cannot contaminate food product, whether directly or indirectly.
Control & instrumentation equipment and in the sanitary installation of cabling.
Protection against moisture, dust and high temperatures
Electronic device are composed of many sensitive parts and therefore they should be placed in locations where they do not put a process at risk. They must be protected from:-
  Things falling or spilling on them
  Moisture and dust
  High room temperatures
Notes: 3

## Slide 4: Hygienic Environment Classifications
Hygienic environment classifications
There are four types of Hygienic environment classifications for food production areas within factories:
  High-High (Nutrition), High, Medium, and Basic.
Following are Factory requirements for electrical installations in Hygienic environments.
Bus- Trunking System and Cable Bus System:
These systems are not permitted to be installed in High hygiene environments and above.
These systems must not be installed directly above production lines.
Notes: 4

## Slide 5: Cable Tray
Good method
Cable trays must be installed in a vertical orientation in Medium hygiene and above environments.
Cable trays must be installed with a minimum clear space of 100mm between the tray and wall or other equipment.
Cable trays must be sized such that they do not contain more than one layer of cables in Medium hygiene and above environments.
Cable tray should not be installed above production lines.
Mounting hardware shall match the material of the cable tray as a minimum.
Notes: 5

## Slide 6: Cable Tray
Good method
Mounting hardware shall match the material of the cable tray as a minimum.
Supports made of threaded rod, and exposed threading of bolts/screws is not permitted.
Gaps between cable tray supports and the supporting structure must be filled and sealed to prevent dust and liquid from settling in the gaps.
Cable tray material and construction requirements are shown in the table below:
 | Hygienic Zone |  |  | 
 | Basic | Medium | High | High/high
Dry area | *GC/EZ | *GC/EZ | 304L SS | 304L SS
Wet area | 316L SS | 316L SS | 316L SS | 316L SS
*GC = hot-dipped galvanized steel; rougher surface than EZ; best for tropical or high humidity locations
*EZ = electro-zinc galvanized steel; smoother surface than GC; better suited for low humidity locations
Notes: 6

## Slide 7: Equipment Enclosures
Lexan, polycarbonate, or acrylic shall be used as a substitute for glass in all production areas. Glass is not permitted (lamps are the exception as long as the fixture housing/enclosure completely contains any potential glass breakage) in production areas.
Enclosures shall be IP66 rated stainless steel in High Hygiene and above environments.
Enclosures in dry production areas must be IP55 rated and be powder coated (RAL 7032) sheet steel.
Conduit:
If the installation of conduit is not avoidable and no other hygienic alternative exists, conduit shall be completely and properly sealed in accordance standards.
Ceiling and wall penetrations in hygienic areas must be sealed with mineral fiber plates and a fire-stop mastic or spray.
Notes: 7

## Slide 8: Lighting Selection & Standard
Lighting
Lighting fixtures shall be protected with shatter proof covers.
Lighting fixtures shall be IP66 rated in production areas if subjected to wash-downs.
Lighting fixtures shall not be installed directly above production lines.
Lighting levels in production areas shall be in accordance with the IEC standards.
Installation Hardware
Unhygienic couplings (Unistrut, etc.) are not permitted in Medium hygiene and above zones.
Hollow bodies are not permitted in Medium hygiene and above environments.
Threaded rod is not permitted in Medium hygiene and above environments.
Exposed threaded couplings are not permitted in Medium hygiene and above environments.
Notes: 8