## Slide 1
Voltage Drop Calculator

## Slide 2
1
IEC requirements
X
About PMG Engineering
Page 3
#
CONTENTS
X

## Slide 3: IEC Requirements
The IEC requirements for voltage drop are as follows:
  IEC 60364-5-52 : 4% of rated voltage
  IEC 60204-1 : 5% of rated voltage
Refer to the local codes for market specific requirements.
The following method can be used to calculate voltage drop (ΔV; in volts) along a conductor path:
  ΔV = k x I x [R x cos θ x Z x sinθ] x L
Notes: 3

## Slide 4: IEC Requirements
Where,
  k = 2 for single-phase systems and √3 for three-phase systems
  I = load current along the conductor pat
  R = resistance; 25Ω per mm2 per kilometer of conductor (copper)
  cosθ = power factor (can use .80 in absence of actual values)
  Z = inductive resistance; 0 for conductors of 50mm2 or less, .08Ω per kilometer of conductor for conductors greater than 50mm2
  sinθ = calculate based on power factor value
  L = conductor length in kilometers (one way, from source to equipment)
For percent voltage drop (ΔV%), use the following equation:
ΔV% = [ΔV x 100] / V
  V = voltage (line-to-neutral for single phase; phase-to-phase for three phase)
Notes: 4