## Read me
PMG ENGINEERING
PMG-D2 · Cold Room & Refrigeration Load Calculator
WHAT THIS DOES
Estimates the refrigeration load of a cold room or chilled space and converts it into the machine capacity you need to buy, by adding up the loads that actually matter: heat through the envelope, air infiltration, the product itself, internal gains, and an allowance for defrost and fan heat.
Use it at concept and basic engineering to size plant, to sanity-check a vendor's selection, and to see which load dominates — which is usually the one worth designing out.
HOW TO USE IT
1. Fill the straw-coloured cells on '1 Inputs'. Grey cells are calculated — do not type in them.
2. Read the result at the top of '2 Load calculation': daily load, required capacity in kW and TR.
3. Check the load split on the same sheet. If infiltration or product pull-down dominates, the answer is usually an operational or layout change, not a bigger machine.
4. Use '3 Reference' for typical values when you do not yet have real ones — and replace them with measured or vendor data before anything is ordered.
BASIS & LIMITATIONS
Steady-state load summation in the conventional form (ASHRAE Handbook — Refrigeration). It sizes plant; it is not a transient pull-down simulation or a substitute for a vendor's selection software.
Product thermal properties use Siebel's approximation from water content. These are approximations — use measured or tabulated values where the duty is critical or the product is unusual.
Infiltration uses the air-change method. For rooms with heavy traffic, high door frequency or open dock doors, model the doorway directly instead — this method will understate it.
No allowance is made for the refrigeration system's own efficiency, pipe losses or part-load behaviour. Size the machine against the required capacity, then check turndown.
REFERENCES
· ASHRAE Handbook — Refrigeration (load calculation and product data chapters)
· IS 661 — Code of practice for thermal insulation of cold storage
· Siebel's equations for specific heat and latent heat of foods from water content
NEED THIS ENGINEERED FOR YOUR FACTORY?
PMG has engineered 250+ food & beverage factories across 15+ markets — from concept layout and hygienic design to detailed engineering, construction supervision and commissioning. info@pmg.engineering · pmg.engineering
Reference material for planning use only. Verify every figure against the governing standards and your own site conditions before acting on it — contact PMG Engineering for expert consultation on your project.
© 2026 PMG Engineering Pvt Ltd · pmg.engineering · info@pmg.engineering

## 1 Inputs
PMG ENGINEERING
PMG-D2 · Cold Room & Refrigeration Load Calculator
Straw cells = enter your values. Grey cells are calculated.
1 ROOM
Internal dimensions. Design ambient is the worst case the plant must hold, not the annual average.
Room length | 20 | m
Room width | 12 | m
Room clear height | 6 | m
Room volume |  | m3
Floor area |  | m2
Wall + ceiling area |  | m2
Room design temperature | 2 | degC
Ambient design temperature (dry bulb) | 43 | degC | Site design condition, not annual mean
Temperature under floor / adjacent | 30 | degC | Ground or adjoining space
2 ENVELOPE
U-value = thermal conductivity / insulation thickness. See '3 Reference' for typical panel selections.
Insulation thickness - walls & ceiling | 100 | mm
Insulation conductivity (k) | 0.022 | W/m.K | PUR/PIR panel typical
U-value - walls & ceiling |  | W/m2.K
Insulation thickness - floor | 100 | mm
U-value - floor |  | W/m2.K
3 PRODUCT
The load the room exists for. Throughput is what ENTERS per day, not what is stored.
Product entering per day | 20000 | kg/day
Product entering temperature | 25 | degC
Product final temperature | 2 | degC
Water content (mass fraction) | 0.75 | 0-1 | Drives specific & latent heat - see '3 Reference'
Freezing point of product | -1 | degC
Specific heat above freezing |  | kJ/kg.K | Siebel
Specific heat below freezing |  | kJ/kg.K | Siebel
Latent heat of freezing |  | kJ/kg | Siebel
Stored mass in room | 60000 | kg | For respiration load - fresh produce only
Respiration heat | 0 | W/tonne | 0 for non-respiring product. See '3 Reference'
4 INFILTRATION & INTERNAL GAINS
Door discipline and lighting are the two internal loads most often underestimated.
Air changes per day | 4 | changes/day | From room volume - see '3 Reference'
Enthalpy difference, outside to room air | 60 | kJ/m3 | From ambient & room conditions - see '3 Reference'
Lighting installed | 4 | W/m2
Lighting hours per day | 8 | h/day
People in room | 2 | persons
Heat per person | 270 | W/person | Typical for moderate work in a chilled room
Occupancy hours per day | 6 | h/day
Evaporator fan power (total) | 3 | kW
Fan running hours per day | 20 | h/day
Other equipment in room (forklifts etc.) | 2 | kW
Other equipment hours per day | 4 | h/day
5 OPERATING & MARGIN
Plant running hours per day | 18 | h/day | Leaves time for defrost - do not use 24
Defrost & miscellaneous allowance | 5 | % | Applied to the load subtotal
Safety margin | 10 | % | A decision to record, not a default
Reference material for planning use only. Verify every figure against the governing standards and your own site conditions before acting on it — contact PMG Engineering for expert consultation on your project.
© 2026 PMG Engineering Pvt Ltd · pmg.engineering · info@pmg.engineering

## 2 Load calculation
PMG ENGINEERING
PMG-D2 · Load calculation
All loads in kWh per day, then converted to the capacity the machine must deliver.
RESULT
Total daily heat load |  | kWh/day
REQUIRED REFRIGERATION CAPACITY |  | kW
REQUIRED REFRIGERATION CAPACITY |  | TR | 1 TR = 3.5169 kW
LOAD BUILD-UP
Watch the split, not just the total: the dominant line is the one worth designing out.
Load component | kWh/day | % of total | Basis
Transmission - walls & ceiling |  |  | U x area x dT x 24 h
Transmission - floor |  |  | U x floor area x dT x 24 h
Air infiltration |  |  | changes/day x volume x dh / 3600
Product - sensible above freezing |  |  | m x cp(above) x dT / 3600
Product - latent (freezing) |  |  | only when the product is frozen
Product - sensible below freezing |  |  | m x cp(below) x dT / 3600
Product - respiration |  |  | stored tonnes x W/tonne x 24 h
Internal - lighting |  |  | W/m2 x floor area x hours
Internal - people |  |  | persons x W x hours
Internal - evaporator fans |  |  | kW x hours
Internal - other equipment |  |  | kW x hours
Subtotal
Defrost & miscellaneous allowance
Safety margin
TOTAL DAILY HEAT LOAD
Reference material for planning use only. Verify every figure against the governing standards and your own site conditions before acting on it — contact PMG Engineering for expert consultation on your project.
© 2026 PMG Engineering Pvt Ltd · pmg.engineering · info@pmg.engineering

## 3 Reference
PMG ENGINEERING
PMG-D2 · Reference values
Typical industry figures for use before real data exists. Replace them before anything is ordered.
TYPICAL PANEL SELECTION BY ROOM TEMPERATURE
Room temperature | Typical insulation thickness | Notes
+10 to +15 C (dry store, ripening) | 60-80 mm | Check condensation risk on the warm face.
0 to +5 C (chilled) | 80-100 mm | The common food chill-room selection.
-18 to -25 C (frozen) | 125-200 mm | Under-floor heating required over an unheated slab.
-30 C and below (blast/hardening) | 200 mm+ | Vapour-barrier detailing becomes critical.
AIR CHANGES PER DAY BY ROOM VOLUME
Indicative ranges - larger rooms change air less often per unit volume. Increase for high door frequency; decrease with an air curtain, lobby or fast-acting door.
Room volume | Changes/day - above 0 C | Changes/day - below 0 C
50 m3 | 13 - 17 | 9 - 13
100 m3 | 9 - 12 | 7 - 9
500 m3 | 4 - 6 | 3 - 5
1,000 m3 | 3 - 4 | 2 - 3
3,000 m3 and above | 1.5 - 2.5 | 1 - 2
TYPICAL WATER CONTENT OF COMMON FOODS
Drives specific heat and latent heat through Siebel's equations. Approximations only - use measured or ASHRAE product-table values where the duty is critical.
Product | Water content (mass fraction) | Notes
Fresh vegetables (leafy) | 0.90 - 0.95 | Respiring - set a respiration load.
Fresh fruit | 0.85 - 0.90 | Respiring - varies with variety and temperature.
Milk | 0.87 | Non-respiring.
Raw meat / poultry | 0.65 - 0.75 | Non-respiring.
Fish | 0.70 - 0.80 | Non-respiring.
Cheese (hard) | 0.35 - 0.40 | Non-respiring.
Bread / bakery | 0.30 - 0.40 | Check staling behaviour separately.
Ice cream | 0.60 - 0.65 | Freezing point well below 0 C - set it explicitly.
RESPIRATION HEAT - FRESH PRODUCE ONLY
Non-respiring products (meat, dairy, baked, frozen, packaged) take zero. Respiration roughly doubles per 10 C rise, so a warm room costs twice.
Produce type | Typical respiration at 0-5 C | Notes
Low - apples, onions, potatoes | 10 - 30 W/tonne | Rises sharply with temperature.
Medium - carrots, cabbage, citrus | 30 - 60 W/tonne
High - leafy greens, beans, sweetcorn | 60 - 150 W/tonne | Can dominate the load in a full room.
Very high - mushrooms, asparagus, broccoli | 150 W/tonne and above | Verify against product data.
Reference material for planning use only. Verify every figure against the governing standards and your own site conditions before acting on it — contact PMG Engineering for expert consultation on your project.
© 2026 PMG Engineering Pvt Ltd · pmg.engineering · info@pmg.engineering